TECHNICAL REQUIREMENTS AND SPECIFICATIONS

# PROTECTIVE COATING OF POTABLE WATER STEEL TANKS, STRUCTURES AND LARGE DIAMETER STEEL PIPELINE

FOREWORD

This specification covers work, materials and equipment required for protecting and/or restoring steel structures by monolithic spray-application of a solvent-free, high-build epoxy coating to eliminate infiltration / exfiltration, provide corrosion protection, repair damaged surfaces and enhance structural integrity. Procedures for surface preparation, cleaning, application and testing are described.

PART 1  GENERAL

1.1	SECTION INCLUDES

    - Solvent-free epoxy coating to be applied to specified surfaces and conforms to the requirements set forth below.

    - This specification covers all labor, materials, equipment and services necessary to complete the installation of corrosion protection for steel surfaces as herein specified.

    - Related Sections:  Steel Repair,  Environmental, Health and Safety.

1.2	REFERENCES

- ASTM D543 - Resistance of Plastics to Chemical Reagents

- ASTM D638 - Tensile Properties of Plastics

- ASTM D695 - Compressive Properties of Rigid Plastics

- ASTM D790 - Flexural Properties of Unreinforced and Reinforced                                 Plastics

- ASTM D2240 - Durometer Hardness, Type D

- ASTM D4541 - Pull-off Strength of Coatings Using a Portable Adhesion Tester

- ASTM - the published standards and test methods of the American Society for Testing and Materials, West Conshohocken, PA.

- NSF/ANSI Standard 61- Drinking  Water System Components.

- NACE - the published standards of National Association of Corrosion Engineers (NACE International), Houston, TX.

- SSPC - the published standards of the Society of Protective Coatings, Pittsburgh, PA.

1.3	SUBMITTALS

A.	The following items shall be submitted:

- Technical data sheet on each product used, including ASTM test results indicating the product conforms to and is suitable for its intended use per these specifications.

- Material Safety Data Sheets (MSDS) for each product used.

- Project specific guidelines and recommendations.

- Applicator Qualifications:

  - Manufacturer certification that the Applicator has been trained in the handling, mixing and application of the products to be used.

  - Certification that the equipment to be used for applying the products has been approved by the protective coating manufacturer and Applicator personnel have been trained and certified for proper use of the equipment.

  - Three (3) years experience and five (5) recent references of Applicator indicating successful application of a 100% solids high-build solvent-free coating by spray application.

  - Proof of any necessary federal, state or local permits or licenses necessary for the project.

- Design details for any additional ancillary systems and equipment to be used in surface preparation, application and testing.

- Or Equal Submittal:  In order to be considered as an equal product, said product will have to meet the minimum characteristics as measured by the applicable  standards referenced in paragraphs 2.03 and 2.04 and on the Technical Data Sheets of the approved products.

  - Note:  Equal products must be approved a minimum of two weeks prior to bid date.  In order for a product to be considered equal the submitted product must meet or exceed the minimum standards included in this specification. A bonded third party testing company must perform the testing.  A contractor that has been licensed and trained by the manufacturer must install all products.

1.4	QUALITY ASSURANCE

A.	Applicator shall initiate and enforce quality control procedures consistent with applicable ASTM, NACE and SSPC standards and the protective coating manufacturer's recommendations.

B.	(OPTIONAL) A NACE Certified Coating Inspector shall be provided by Owner.  The Inspector will observe daily operations, procedures and final product to ensure adherence to the specifications by Applicator.

1.5	DELIVERY, STORAGE, AND HANDLING

A.	Materials are to be kept dry, protected from weather and stored under cover.

B.	Protective coating materials are to be stored between 50 and 90 deg F.   Do not store near flame, heat or strong oxidants.

C.	Protective coating materials are to be handled according to their material safety data sheets.

1.6	SITE CONDITIONS

A.	Applicator is to conform with all local, state and federal regulations including those set forth by OSHA, RCRA and the EPA and any other applicable authorities.

B.	Method statements and design procedures are to be provided by Owner when confined space, lock-out, flow diversion or bypass is necessary in order for Applicator to perform the specified work.

1.7	WARRANTY

A.	Applicator shall warrant all work against defects in materials and workmanship for a period of one (1) year, unless otherwise noted, from the date of final acceptance of the project.  Applicator shall, within a reasonable time after receipt of written notice thereof, make good defects in materials or workmanship which may develop during said one (1) year period, and any damage to other work caused by such defects or the repairing of same, at his own expense and without cost to the Owner.

PART 2  PRODUCTS

2.1	EXISTING PRODUCTS

- Specified steel surfaces will be thoroughly inspected.

- (OPTIONAL) After blast preparation surfaces may be ultrasonically tested to detect thin spots in the shell where the structural integrity of the structure has deteriorated.  After blast preparation these spots should be marked with epoxy spray paint or zinc primer.

C.	Existing coatings should be removed or, where bonded well, thoroughly abraded to provide adequate surface profile for mechanical bond by the new protective coating.  Applicator is to maintain strict adherence to the protective coatings manufacturer's recommendations with regard to proper surface preparation and compatibility with existing coatings.

2.2	MANUFACTURER

- Raven Lining Systems, Broken Arrow, Oklahoma  800-324-2810 or 918-615-0140 FAX.

2.3	REPAIR MATERIALS

A.	Repair materials used to fill pits prior to protective coating application must be accepted and approved for compatibility with the specified epoxy coating and be certified to the requirements of ANSI/NSF Standard 61- Drinking  Water System Components.

B.	As an example, the following products could be used within the specifications:

- Raven Lining System’s AquataPoxy A-6 Thick or A-61 100% solids solvent-free epoxy which can be spray applied then leveled witha putty knife, trowel or applied directly with a putty knife or trowel ect.

- (OPTIONAL) Fiberglass woven roving fabric, 9 oz/yd2, 30" bias.

2.4	PROTECTIVE COATING MATERIAL

- Coating products shall be applied to all interior surfaces to protect the host substrate and repair materials that are free of structural movement from all forms of chemical or bacteriological attack and to impart a degree of structural enhancement.

- Coating product physical properties shall be substantiated through submittal of accredited third party testing results and shall be representative of the actual field applied product and cure mechanism(s) to be employed in the field

- Epoxy coating system - 100% solids, solvent-free two-component epoxy, certified to meet the requirements of NSF/ANSI Standard 61 - Drinking  Water System Components.

      - Manufacturer: Raven Lining Systems, Broken Arrow, Oklahoma 800-324-2810 or 918-615-0140 fax.

      - Product: AquataPoxy A-6 /A-6 Thick

        - Product type			Amine cured epoxy

        - Color				White

        - Solids Content (vol %)	100

        - Mix Ratio			1:1

        - Hardness, Shore D (ASTM D2240):>87

        - Compressive Strength, (ASTM D695):>10,000 psi

        - Tensile Strength, (ASTM C638):>6,000 psi

        - Flexural Strength, (ASTM D790):>9,400 psi

        - Adhesion, (ASTM D4541): >930 psi

        - VOC’S 0.0 lbs/gal

- Epoxy coating system - 100% solids, solvent-free two-component epoxy, certified to meet the requirements of NSF/ANSI Standard 61 - Drinking  Water System Components.

      - Manufacturer: Raven Lining Systems, Broken Arrow, Oklahoma 800-324-2810 or 918-615-0140 fax.

      - Product: AquataPoxy A-61

        - Product type			Amine cured epoxy

        - Color				Aqua, or Brown

        - Solids Content (vol %)	100

        - Mix Ratio			3:1

        - Hardness, Shore D (ASTM D2240):>88

        - Compressive Strength, (ASTM D695):>16,600 psi

        - Tensile Strength,  (ASTM C638):>7,700 psi

        - Flexural Strength,  (ASTM D790):>10,600 psi

        - Adhesion, (ASTM D4541): >2500 psi

        - VOC’S 0.0 lbs/gal

2.5	PROTECTIVE COATING APPLICATION EQUIPMENT

- Manufacturer approved heated plural component spray equipment shall be  uses in the application of the specified protective coating.

PART 3  EXECUTION

3.1	ACCEPTABLE APPLICATORS

A.	Protective coating must be applied by a Certified Applicator of the protective coating manufacturer and according to manufacturer specifications.

3.2	EXAMINATION

A.	All structures to be coated shall be readily accessible to Applicator.

B.	Appropriate actions shall be taken to comply with local, state and federal regulatory and other applicable agencies or client specific policies with regard to environment, health and safety.

C.	Any active flows shall be locked-out, plugged or diverted as required to ensure that the liquid flow is maintained below the surfaces to be coated.  Any equipment shall be locked-out according to site safety and OSHA requirements.

D.	Temperature of the surface to be coated should be maintained between 40 deg F and 120 deg F during application.  The surface temperature of the steel should be maintained at a minimum of 5 deg F above dewpoint during application.

3.3	SURFACE PREPARATION

A.	Applicator shall inspect all surfaces specified to receive a protective coating prior to surface preparation.  Applicator shall notify Owner of any noticeable disparity  in the surfaces which may interfere with the proper preparation or application of the protective coating.

B.	Surfaces shall be free of weld splatter.  All welds shall be continuous.

C.	Steel contaminated with soluble salts (ie. chlorides and sulfates) develops flash rust rapidly at intermediate and high humidities.  Therefore, these salts must be removed from the steel surface preferably before blast cleaning and by eliminating sources of recontamination during and after blast cleaning.  A number of tests for soluble salts have been examined by SSPC, ASTM, the National Shipbuilding Research Program, and the International Organization for Standardization.

(This information was taken from NACE No. 1.  Refer to this Standard for additional information.)

D.	All loose scale, large deposits oil, grease, cutting oils, dirt and other contaminants shall be removed prior to abrasive blasting by washing with detergent and potable water, followed by a thorough rinsing with potable water.

E.	The steel surfaces to be coated shall be abrasive blast cleaned.  Blast air shall be free of oil and water.

F.	Abrasive shall be steel grit (G-40 size), steel shot (S-230 size), graded flint, black beauty or equal (30-60 mesh).  Abrasive shall not be recycled.

G.	Abrasive blasting shall not be performed when the air or steel temperature is below 40 deg F, when the relative humidity exceeds 80%, or when the steel is less than 5 deg F warmer than the dewpoint.  The Contractor will provide dehumidification, and/or temperature control as necessary to meet these conditions.

H.	Blast cleaning shall be in accordance with SSPC-SP 5, White Metal Blast Cleaning for severe-duty immersion service of the coated areas.  Blast cleaning for other surfaces shall be in accordance with SSPC-SP 10, Near White Blast Cleaning.  Anchor profile shall be 2.5-5.0 mil and relative to the coating thickness specified.

I.	Remove all blasting residues from the structure/vessel by means of vacuum cleaning plus, as appropriate, shovels, brooms, clean compressed air, vacuum cleaners and other dry extraction methods.

J.	All surfaces should be throughly inspected and when necessary, ultrasonically tested to detect thin spots in the structure which need reinforcement before the protective coating is applied.

  - REPAIR OF STEEL

A.	All pits representing 20% to 50% metal loss are to be filled with AquataPoxy A-6 Thick or A-61 100% solids solvent-free epoxy grout. Use pressure to apply with putty knife, trowel or gloved hand and wipe smooth.

B.	A fiberglass fabric patch shall be applied whenever corrosion or errosion (50% of original thickness. A repair patch with a minimum radius of one foot outside of the edge of the thin area shall be applied. A prime coat of AquataPoxy A6/A-6 thick or A-61 epoxy shall be applied to the patch area until a 40-80 mil thickness is achieved. Prior to gelation of the prime coat, sheets of 9 oz/yd2, 30" bias fiberglass fabric should be rolled into the prime coat until fully wetted and embedded including all edges and loose fibers. After the epoxy with fiberglass has gelled and is solid to the touch (but not longer than the recoat window) loose fibers should be trimmed or ground smooth. Protective coating should then be applied as described in Section 3.05.

3.5	APPLICATION OF PROTECTIVE COATING

- Application procedures shall conform to the recommendations of the protective coating manufacturer, including material handling, mixing, environmental controls during application, safety, and spray equipment.

B.	Before spraying any coating, all welds, grooves, other rough areas, difficult-to-spray areas, and repair areas as specified shall be striped with AquataPoxy A-6/A-6 Thick or A-61 epoxy to a 5 to 8 mil thickness.  Striping can be accomplished by spray application in accessible areas; and, hand-mixing product or spray followed by scrub-striping with a good-quality bristle brush in difficult-to-spray areas.

C.	The spray equipment shall be specifically designed to accurately ratio and apply the specified protective coating materials in accordance with coating manufacturer’s requirements and shall be regularly maintained and in proper working order.

D.	The protective coating material must be spray applied by a Certified Applicator of the protective coating manufacturer.

    - Specified surfaces shall be coated with one or more coats of A-6 Thick with a  total Dry Film Thickness of 16 to 80 mils depending on service conditions and surface profile, one coat of A-61 with a  total Dry Film Thickness of 25 to 80 mils depending on service conditions and surface profile or multiple coats of A-6, each coat being 5 to 10 mils thick, to achieve a Dry Film Thickness of between 16 and 80 mils depending on service conditions and surface profile.

      - Each coat of the A-6/A-6 Thick protective coating should occur as soon as the basecoat becomes tack free, but no later than the recoat window for the specified product. Additional surface preparation procedures will be required if this recoat window is exceeded.

      - A-61 protective coating should be applied to the desirerd mil thickness in one coat. Additional surface preparation procedures will be required if  additional appliactions are required.

      - See coating manufacture for mil thickness recommendations to ground water head pressure.

    - (Pipeline only) Coating product(s) shall interface with adjoining construction materials throughout the pipeline to effectively seal and protect steel substrates from infiltration and attack by corrosive elements.  Procedures and materials necessary to effect this interface shall be as recommended by the coating product(s) manufacturer.

    - (Pipeline only) Termination points of the coating product(s) shall be made at each manhole joint, 1” below normal flow levels (when less than 360o coating application is being specified), and a minimum of 1” interfacing with each pipe penetration.  When less than 360o of the pipe is to be coated, the coating shall be terminated within the pipe.

    - Surfaces not to receive the coating shall be masked or otherwise protected to prevent overspray or feathering of the coating termination.

F.	(OPTIONAL) Sloped surfaces of the floor may be made non-skid by broadcasting aluminum oxide or silica sand into the surface prior to gelation.

3.7	TESTING AND INSPECTION OF PROTECTIVE COATING

A.	During application a wet film thickness gauge, such as those available through Paul N. Gardner Company, Inc. meeting ASTM D4414 - Standard Practice for Measurement of Wet Film Thickness of Organic Coatings by Notched Gages, shall be used to ensure a monolithic coating and uniform thickness during application.

B.	After the protective coating has set hard to the touch it shall be inspected with high-voltage holiday detection equipment.  The spark tester shall be initially set at 100 volts per 1 mil (25 microns) of film thickness applied but may be adjusted as necessary to detect the induced holiday (refer to NACE RPO188-99).  All detected holidays shall be marked and repaired by abrading the coating surface with abrasive paper or brush blast.  After abrading, additional protective coating material can be hand applied to the repair area, but should not be applied beyond the abraded area.  All touch-up/repair procedures shall follow the protective coating manufacturer's recommendations.

C.	Measure the coating thickness with an ultrasonic thickness gauge to ensure that the required DFT has been applied.  Repair low DFT by application of additional coating.

D.	Measurement of adhesion strength of the protective coating to the substrate can be made at regular intervals and along different sections of the structure. Adhesion strength can be measured in accordance with ASTM D4541.  Any areas detected to have inadequate adhesion strength shall be evaluated by the Project Engineer.  Further adhesion tests may be performed in that area to determine the extent of the potentially deficient bonded area and repairs should be made by the Applicator in strict accordance with manufacturer's recommendations.

E.  	A final visual inspection shall be made by the Inspector and manufacturer's representative.  Any deficiencies in the finished coating shall be marked and repaired according to the procedures set forth herein by Applicator.

F.	If AquataPoxy A-6/A-6 Thick epoxy was the product used the system may be put back into service in 3 days at 77F in accordance with NSF/ANSI Standard 61 Certification.

G.	If AquataPoxy A-61 epoxy was the product used the system may be put back into service in 5 hours at 72F in accordance with NSF/ANSI Standard 61 Certification

END OF SECTION