TECHNICAL REQUIREMENTS AND SPECIFICATIONS

FOR THE CORROSION PROTECTION AND/OR REHABILITATION

OF STORM WATER LARGE DIAMETER STEEL PIPELINE AND STEEL

STRUCTURES

FOREWORD

This specification covers work, materials and equipment required for protecting and/or restoring steel structures by monolithic spray-application of a solvent-free, high-build epoxy coating to eliminate infiltration / exfiltration, provide corrosion protection, repair damaged surfaces and enhance structural integrity. Procedures for surface preparation, cleaning, application and testing are described.

- GENERAL

  - SUMMARY

    - Solvent-free epoxy coating to be applied to specified surfaces and conforms to the requirements set forth below.

    - This specification covers all labor, materials, equipment and services necessary to complete the installation of corrosion protection for steel surfaces as herein specified.

    - Related Sections: Steel Repair,  Environmental, Health and Safety

  - REFERENCES

    - ASTM - the published standards and test methods of the American Society  for Testing and Materials, West Conshohocken, PA.

      - ASTM D543 - Resistance of Plastics to Chemical Reagents

      - ASTM D638 - Tensile Properties of Plastics

      - ASTM D695 - Compressive Properties of Rigid Plastics

      - ASTM D790 - Flexural Properties of Unreinforced and Reinforced       Plastics

      - ASTM D2584 - Volatile Matter Content

      - ASTM D2240 - Durometer Hardness, Type D

      - ASTM D4417 - Field Measurement of Surface Profile of Blast Cleaned Steel

      - ASTM D4414 - Standard Practice for Measurement of Wet Film Thickness of Organic Coatings by Notched Gages

      - ASTM D4541 - Pull-off Strength of Coatings Using a Portable Adhesion Tester

    - NACE - The published standards of National Association of Corrosion Engineers (NACE International), Houston, TX.

      - NACE RPO 188-99 Discontinuity (Holiday) Testing of New Protective Coatings on Conductive Substrates

    - SSPC - The published standards of the Society of Protective Coatings, Pittsburgh, PA.

      - SSPC-SP 1 – Solvent Cleaning

      - SSPC-SP 5 - White Metal Blast Cleaning

      - SSPC-SP 10 - Near White Metal Blast Cleaning

      - SSPC-SP 12 - Surface Preparation and Cleaning of Metals by Water jetting prior to Recoating

      - SSPC-PA 2 - Measurement of Dry Coating Thickness with Magnetic Gages

  - SUBMITTALS

    - Product Data:

      - Technical data sheet for each repair and coating product to be used; including application, cure time, surface preparation procedures, and certification from coating product manufacturer as to the compatibility of the repair material(s) and coating system.

      - Material Safety Data Sheet (MSDS) for each product to be used.

      - Copies of independent testing performed on the coating product indicating the product meets the requirements as specified herein.  Coating product physical properties shall be substantiated through submittal of testing results as documented by an accredited third party laboratory and shall be representative of the actual field applied product  including cure mechanism(s) as to be employed in the field.

      - Three (3) years experience and five (5) recent references of Applicator indicating successful application of a 100% solids high-build solvent-free coating by spray application.

    - Contractor Data:

      - Current documentation from repair and coating product manufacturer(s) certifying Contractor’s training and equipment complies with the Quality Assurance requirements specified herein (Section 1.4).

      - Documentation of requirements of Section 1.6 B & C.

  - QUALITY ASSURANCE

    - Coating and repair product(s) shall be capable of being installed and curing properly within the specified environment(s); Coating product(s) shall be resistant to all forms of chemical or bacteriological attack found in the specified storm water environment(s).

    - Coating and Repair product(s) shall be fully compatible; including ability to bond effectively (as tested for in Section 3.5 C.) to each other and/or the host substrate, forming a composite system.

    - Contractor shall utilize equipment for the application of the coating and repair product(s) which has been approved by the product manufacturer; and Contractor shall have received training on the operation and maintenance of said equipment from the product manufacturer.  Written certification of such approval(s) and training shall be submitted by the coating and repair product manufacturer(s).

    - Contractor and contractor personnel shall be certified by, or have their training approved and certified by, the coating and repair product(s) manufacturer(s) for the handling, mixing, application and inspection of the product(s) to be used as specified herein.  Written certification of such training shall be submitted by the coating and repair product manufacturer(s) and shall include the individual contractor personnel to be employed on the project.

    - Inspectors shall be trained in the use of testing or inspection instrumentation and knowledgeable of the proper use, preparation and installation of the product(s) to be used as specified herein.

    - Contractor shall initiate and enforce quality control procedures consistent with the coating product(s) manufacturer recommendations and applicable NACE, SSPC, ICRI or other standards as referenced herein.

    - Pre-construction meeting shall take place no less than two weeks prior to Contractor mobilization.  All parties to have physical presence on the project during construction shall be present.  At this meeting responsibilities and authorities during construction shall be discerned; comments and questions regarding materials and execution of these specifications shall be presented and addressed.

  - DELIVERY, STORAGE, AND HANDLING

    - Materials are to be kept dry, protected from weather, and stored under cover.

    - Coating and repair materials are to be stored between 50 °F and 90 ° F.  Do not store near flame, heat, or strong oxidants.

    - All materials are to be handled according to their material safety data sheets.

  - SITE CONDITIONS

    - Contractor shall conform to all local, state, and federal regulations including those set forth by OSHA, RCRA and the EPA and any other applicable authorities.

    - Confined space entry program and other required safety training certifications shall be submitted by Contractor to Owner as necessary to perform the specified work.

    - Flow diversion and/or bypass plans shall be submitted by Contractor to Owner as necessary to perform the specified work.

  - WARRANTY

    - Contractor shall warrant all work against defects in materials and workmanship for a period of one (1) year, unless otherwise noted, from the date of final acceptance of the project.  Contractor shall, within a reasonable time after receipt of written notice thereof, repair defects in materials or workmanship which may develop during said one (1) year period, and any damage to other work caused by such defects or the repairing of same, at his own expense and without cost to the Owner.

    - Coating and repair product supplier(s) shall warrant all coating materials for a period of one (1) year from the date of final acceptance, unless otherwise noted, to be free of manufacturing defects; and products will meet current published physical properties when applied and tested in accordance with the manufacturer’s standards.  If, within said one (1) year period, any product does not meet the physical properties or is defective in manufacture the manufacturer will either replace the defective product or refund the purchase price.

- PRODUCTS

  - EXISTING PRODUCTS

    - Specified steel surfaces will be thoroughly inspected.

    - Existing coatings shall be removed which may affect the performance and adhesion of the specified coating product(s).  Contractor is to maintain strict adherence to the protective coatings manufacturer's recommendations with regard to proper surface preparation and compatibility with existing coatings.

    - Thoroughly clean and prepare existing products/surfaces to effect a seal with and promote the adhesion of the coating product(s).

    - (OPTIONAL) After blast preparation surfaces may be ultrasonically tested to detect thin substrate thickness where corrosion or erosion has occured.  The engineer shall evaluate substrate thickness to determine needed applicable repair(s) as necessary; repairs may include the use of welded repairs and/or fiberglass inlay into the coating as per Section 2.2 B.2. and 3.3 E.

  - REPAIR PRODUCTS

    - Repair products shall be used to fill voids or bugholes, smooth transitions between components, replace lost mortar in masonry structures, smooth rough surfaces, and rebuild severely deteriorated substrates and/or to remediate infiltration prior to the installation of the coating product(s).

      - Repair materials must be supplied by the coating product(s) manufacturer or shall be expressly approved by the coating product(s) manufacturer in writing for compatible with the specified coating product(s).

      - All materials shall be mixed, applied, and cured in accordance with the manufacturer’s recommendations.

      - Repair product physical properties shall be substantiated through submittal of accredited third party testing results and shall be representative of the actual field applied product and cure mechanism(s) to be employed in the field.

    - The following products may be accepted and approved as compatible repair and resurfacing products for use within the specifications to repair and/or reinforce substrate defects:

      - 100% solids, solvent-free epoxy grout; specifically the specified coating product(s) (Section 2.3 C.) enhanced with Raven 200 polyolefin fiber filler or other approved aggregate.

      - 100% Solids, Solvent-Free, Ultra-High Build Epoxy Coating to be trowel or otherwise manually applied to interior surfaces.

        - Manufacturer: Raven Lining Systems, Broken Arrow, Oklahoma 800-324-2810 or 918-6150-140 fax.

        - Product:  Raven 405 Trowel – 100% solids, three component (Parts A:B:&C) solvent-free ultra high-build epoxy system.

- Product Type:  amine cured epoxy

- VOC Content (ASTM D2584):  0%

- Compressive Strength, (ASTM D695): >11,200 psi

- Compressive Strength without part C , (ASTM D695): >18600 psi

- Tensile Strength, (ASTM D638): >4,000 psi

- Tensile Strength without part C, (ASTM D638):  >4,900 psi

- Flexural Modulus, (ASTM D790): >806,000 psi

- Flexural Modulus without part C, (ASTM D790):  >810,000

- Adhesion to Concrete, (ASTM D4541): >1000 psi

- Chemical Resistance (ASTM D543/G20) immersion service for:

- Municipal sanitary sewer environment

- Sulfuric Acid, 30%

- Sodium Hydroxide, 10%

- Sodium Hypochlorite, 3%

      - Hydrophobic or Hydrophilic injectable urethane chemical grout to be used for the remediation of high volume infiltration or crack repair and/or soil stabilization and void filling.

        - Manufacturer: As applicable

        - Product: Chemical grout as appropriate for infiltration, crack repair and soil stabilization.

      - (OPTIONAL) Fiberglass woven roving cloth using E-Glass, 9 oz/yd2 minimum weight; typical of Hexcel or BFG Industries style #7500.

  - COATING PRODUCTS

    - Coating product shall be applied to all interior surfaces to protect the host substrate and repair materials from all forms of chemical or bacteriological attack typically found in the specified environment(s) and to impart a degree of structural enhancement.

    - Coating product physical properties shall be substantiated through submittal of accredited third party testing results and shall be representative of the actual field applied product and cure mechanism(s) to be employed in the field.

    - 100% Solids, Solvent-Free, Ultra-High Build Epoxy Coating to be spray applied to all interior surfaces above the spring line or as otherwise detailed.

      - Manufacturer: Raven Lining Systems, Broken Arrow, Oklahoma 800-324-2810 or 918-615-0140 fax.

      - Product:  Raven 405 – 100% solids, solvent-free ultra high-build epoxy system exhibiting the following characteristics:

        - Product Type:  amine cured epoxy

        - VOC Content (ASTM D2584):  0%

        - Compressive Strength, (ASTM D695): >18,000 psi

        - Tensile Strength, (ASTM D638): >7,500 psi

        - Flexural Modulus, (ASTM D790): >700,000 psi

        - Adhesion to Steel, (ASTM D4541): >1000 psi

        - Chemical Resistance (ASTM D543/G20) immersion service for:

- Municipal sanitary sewer environment

- Sulfuric Acid, 30%

- Sodium Hydroxide, 10%

- Sodium Hypochlorite, 12.5%

        - Successful Pass: Sanitation District of L.A. County Coating Evaluation Study and SSPWC 210.2.3.3 (Greenbook “Pickle Jar” Chemical Resistance test)

    - 100% Solids, Solvent-Free, Ultra-High Build Epoxy Coating to be spray applied to all interior surfaces above the spring line or as otherwise detailed.

      - Manufacturer: Raven Lining Systems, Broken Arrow, Oklahoma 800-324-2810 or 918-615-0140 fax.

      - Product:  Raven 405 FS – 100% solids, solvent-free ultra high-build epoxy system.

        - Product Type:  amine cured epoxy

        - VOC Content (ASTM D2584):  0%

        - Compressive Strength, (ASTM D695): >16,000 psi

        - Tensile Strength, (ASTM D638): >7,600 psi

        - Flexural Modulus, (ASTM D790): >688,000 psi

        - Adhesion to Steel, (ASTM D4541): >1000 psi

        - Chemical Resistance (ASTM D543/G20) immersion service for:

- Municipal sanitary sewer environment

- Sulfuric Acid, 30%

- Sodium Hydroxide, 10%

- Sodium Hypochlorite, 3%

  - PRODUCT APPLICATION EQUIPMENT

    - Coating product to be spray applied shall be mixed and applied using manufacturer approved heated plural component spray equipment.

    - Coating product application to hard to reach areas or for touch-up may be performed using hand tools.

- EXECUTION

  - EXAMINATION

    - Appropriate actions shall be taken by Contractor to comply with local, state, and federal regulatory and other applicable agencies with regard to environment, health, and safety during work.

    - All structures to be coated shall be readily accessible to Contractor.

    - Any active flows shall be dammed, plugged, or diverted as required to ensure all liquids are maintained below or away from the surfaces to be coated until final applications are cured as recommended by the manufacturer.

    - Temperature of the surface to be coated should be maintained between 40 deg F and 120 deg F during application. The surface temperature of the steel should be maintained at a minimum of 5 deg F above dewpoint during application.

    - Prior to commencing surface preparation, Contractor shall inspect all surfaces specified to receive the coating and notify Owner, in writing, of any noticeable disparity in the site, structure or surfaces which may interfere with the work, use of materials or procedures as specified herein.

  - SURFACE PREPARATION

    - Surfaces shall be free of weld splatter. All welds shall be   continuous.

    - Excessive debris, sediment, root intrusion or other foreign materials which may impact the effectiveness of the surface preparation process shall be removed prior to the commencement thereof.

    - Oils, grease, incompatible existing coatings, waxes, form release, curing compounds, efflorescence, sealers, salts, or other contaminants which may affect the performance and adhesion of the coating to the substrate shall be removed in accordance with SSPC-SP 1 – Solvent Cleaning.

    - Choice of surface preparation method(s) should be based upon the condition of the structure and substrate, potential contaminants present, access to perform work, and the required cleanliness and profile of the prepared surface to receive the repair and/or coating product(s).

    - Steel contaminated with soluble salts (ie. chlorides and sulfates) develops flash rust rapidly at intermediate and high humidities.  Therefore, these salts must be removed from the steel surface preferably before blast cleaning and by eliminating sources of recontamination during and after blast cleaning.  A number of tests for soluble salts have been examined by SSPC, ASTM, the National Shipbuilding Research Program, and the International Organization for Standardization.  (This information was taken from NACE No. 1.  Refer to this Standard for additional information.)

    - Steel surfaces to be coated shall be abrasive blast cleaned.

      - Blast air shall be free of oil and water.

      - Abrasive shall be as required to produce the specified level of cleanliness and profile in an efficient and uniform manner.  Abrasive shall not be recycled.

      - Abrasive blasting shall not be performed when the air or steel temperature is below 40 °F, when the relative humidity exceeds 80%, or when the steel is less than 5 °F warmer than the dew point.  The Contractor will provide dehumidification, and/or temperature control as necessary to meet these conditions.

      - Blast cleaning shall be in accordance with SSPC-SP 5, White Metal Blast Cleaning for immersion service of the coated areas.  Blast cleaning for other surfaces shall be in accordance with SSPC-SP 10, Near White Blast Cleaning.  Anchor profile shall be 2.5-5.0 mils and relative to the coating thickness specified.

        - Anchor profile shall be measured and recorded according to ASTM D4417 Standard Test Methods for Field Measurement of Surface Profile of Blast Cleaned Steel, Method C.

      - Alternatively, surfaces to be recoated may be cleaned according to SSPC-SP 12/NACE No. 5 - Surface Preparation and Cleaning of Metals by Water jetting prior to Recoating.

        - Preparation shall be to SSPC-SP 12, WJ-1, and Clean to Bare Substrate using a minimum of High-Pressure Water Jetting (10,000 psi-30,000 psi).

        - Water jetting does not produce a profile of the magnitude currently recognized by the coatings industry.  Rather, it exposes the original abrasive-blasted surface profile if one exists.  An anchor profile of at least 2.5 mils is required to be exposed.  If sufficient profile does not exist, abrasive blasting shall be performed as specified in section 3.2 D.

        - At the time of the recoating, the amount of flash rust shall be no greater than “No Flash Rust” as defined in SSPC-SP 12.

        - If inhibitors are to be used with the standard jetting water, the coatings manufacturer shall be consulted to ensure the compatibility of inhibitors with the coatings.

    - Remove all blasting residues from the structure/vessel by means of vacuum cleaning plus, as appropriate, shovels, brooms, clean compressed air, vacuum cleaners and/or other dry extraction methods.

    - All surfaces should be inspected by the Inspector during and after preparation and before the coating is applied.

  - APPLICATION OF REPAIR PRODUCTS

    - Repair products shall be used to fill voids, pinholes, and other surface defects which may affect the performance or adhesion of the coating product(s).

    - Repair products shall be installed to minimum thickness as recommended within manufacturers published guidelines.  Should structural repairs be necessary, these products shall be installed as specified by the Project Engineer.

    - Repair products shall be handled, mixed, installed and cured in accordance with manufacturer guidelines.

    - All repaired surfaces shall be inspected for cleanliness and suitability to receive the coating product(s).  Additional surface preparation may be required prior to coating application.

    - (Optional)  Fiberglass woven roving cloth may be rolled into the coating for added tensile and flexural strength where desired and/or required.

      - A tack coat of a minimum of 20-30 mils shall be applied and allowed to cure to a tack free state, followed by and additional coat of 20-30 mils of coating into which the fiberglass matte shall be inlayed and rolled while wet, an additional 50-60 mil coat minimum shall be applied over the fiberglass inlay as part of the overall coating application.

      - Fiberglass matte shall be woven roving cloth with an approximate weight of 9 oz/yd2.  Fiberglass matte shall be rolled into the epoxy tack coat(s) using a notched roller fully relieving trapped air and wrinkles.  The final topcoat shall encapsulate all fiberglass strands.  Care should be taken to ensure adequate cure time between applications above 100 mils to relieve exothermic heat in order to avoid thermal degradation of the coating.

  - APPLICATION OF COATING PRODUCT(S)

    - Application procedures shall conform to the recommendations of the coating product(s) manufacturer, including environmental controls, product handling, mixing, application equipment and methods.

    - Spray equipment shall be specifically designed to accurately ratio and apply the coating product(s) and shall be in proper working order.

    - Contractors qualified in accordance with Section 1.4 of these specifications shall perform all aspects of coating product(s) installation.

    - Prepared surfaces shall be coated via spray application of the coating product(s) described herein unless otherwise recommended by the coating product manufacturer.

    - Before spraying any coating, all welds, grooves, pits, other rough areas, difficult-to-spray areas, and other areas as specified shall be striped.   Striping can be accomplished by spray application in accessible areas; and, hand-mixing product or spray followed by scrub-striping with a good-quality bristle brush in difficult-to-spray areas.

    - Prepared surfaces shall be coated by spray application of the coating product(s) described herein to a minimum wet film thickness of 60 mils or greater as necessary to compensate for corrosion pitting. (Thickness shown below are for general purposes only, each project should be evaluated independently and thickness of system determined upon product, service environment, protection and restoration requirements:  60-100 mils for immersion; 40-60 mils for atmospheric, or 60-80 for splash and spill exposure)

    - Subsequent topcoating or additional coats of the coating product(s) shall occur within the products recoat window.  Additional surface preparation procedures will be required if this recoat window is exceeded.

    - Coating product(s) shall interface with adjoining construction materials/components throughout the manhole structure to effectively seal and protect substrates from attack by corrosive elements and to ensure the effective elimination of infiltration into the sewer system.

    - Procedures and materials necessary to effect the interface between dissimilar materials and the coating product shall be as recommended by the coating product(s) manufacturer.

    - (Pipeline only) Coating product(s) shall interface with adjoining construction materials throughout the pipeline to effectively seal and protect steel substrates from infiltration and attack by corrosive elements.  Procedures and materials necessary to effect this interface shall be as recommended by the coating product(s) manufacturer.

    - (Pipeline only) Termination points of the coating product(s) shall be made at each manhole joint, 1” below normal flow levels (when less than 360o coating application is being specified), and a minimum of 1” interfacing with each pipe penetration.  When less than 360o of the pipe is to be coated, the coating shall be terminated within the pipe.

    - Surfaces not to receive the coating shall be masked or otherwise protected to prevent overspray or feathering of the coating termination.

    - Flow shall be stopped, bypassed, or diverted as necessary for application of the coating product(s) to the invert and interface with pipe materials.

  - TESTING AND INSPECTION OF PROTECTIVE COATING

    - Coating system thickness shall be inspected to ensure compliance with the specifications herein.

      - During application a wet film thickness gauge, meeting ASTM D4414 - Standard Practice for Measurement of Wet Film Thickness of Organic Coatings by Notched Gages, shall be used.  Measurements shall be taken, documented, and attested to by Contractor for submission to Owner.

      - After the coating product(s) have cured in accordance with manufacturer recommendations, coating system thickness may be measured according to SSPC-PA 2 - Measurement of Dry Coating Thickness with Magnetic Gages.

    - High voltage holiday detection for coating systems installed in corrosive environments, when it can be safely and effectively employed, shall be performed to ensure monolithic protection of the substrate.  After the coating product(s) have cured in accordance with manufacturer recommendations, all surfaces shall be inspected for holidays in accordance with NACE RPO 188-99 Discontinuity (Holiday) Testing of New Protective Coatings on Conductive.  All detected holidays shall be marked and repaired according to the coating product(s) manufacturer’s recommendations.

      - Test voltage shall be a minimum of 100 volts per mil of coating system thickness.

      - Detection of a known or induced holiday in the coating product shall be confirmed to ensure proper operation of the test unit.

      - All areas repaired shall be retested following cure of the repair material(s).

      - In instances where high voltage holiday detection is not feasible a close visual inspection shall be conducted and all possible holidays shall be marked and repaired as described above.

      - Documentation of areas tested, equipment employed, results, and repairs made shall be submitted to the Owner/Engineer by Contractor.

    - Adhesion of the coating system to the substrate may be confirmed at regular intervals and along different sections of the structure, or for large structures once every 1000 square feet of coated area.  After the coating product(s) have cured in accordance with manufacturer recommendations, testing shall be conducted in accordance with ASTM D4541 - Pull-off Strength of Coatings Using a Portable Adhesion Tester.  Owner’s representative shall select the areas to be tested.

      - For each test area a minimum of three 20 mm dollies shall be affixed to the coated surface, or for large structures a minimum of three 20 mm dollies shall be affixed to the coated surface at random locations within each 1000 square foot area or as otherwise agreed upon.

      - The adhesive used to attach the dollies to the coating shall be rapid setting with tensile strengths in excess of at least twice the anticipated failure point (generally 1000 psi) and permitted to cure in accordance with manufacturer recommendations.  The coating and dollies shall be adequately cleaned and prepared to receive the adhesive.  Failure of the dolly adhesive shall be deemed a non-test and require retesting.

      - Prior to performing the pull test, the coating shall be scored to the substrate, or within 10 mils of the substrate surface, by mechanical means without disturbing the dolly or coating system bond within the test area.

      - Two of the three adhesion pulls in each test area shall exceed 500 psi.

      - Should a structure, or area, fail to achieve two successful pulls as described above, additional testing shall be performed at the discretion of the Owner or Project Engineer.  Any areas detected to have inadequate bond strength shall be evaluated by the Project Engineer.  Further bond tests may be performed in that area to determine the extent of potentially deficient bonded area and repairs shall be made by Contractor.

      - All adhesion testing shall be performed by qualified personnel using calibrated equipment as specified by the applicable ASTM standard(s).

      - All adhesion testing shall be documented and submitted in a consistent format detailing location, test values, description of the failure point/mode, scoring method employed, adhesive used, cure time of coating and adhesive and other data as deemed necessary by the owner/engineer.

      - All adhesion test locations shall be repaired by the Contractor at no cost to the Owner.

    - Visual inspection shall be made by the Project Engineer and/or Inspector.  Any deficiencies in the finished coating affecting the performance of the coating system or the operational functionality of the structure shall be marked and repaired according to the recommendations of the coating product(s) manufacturer.

    - The system may be returned to full operational service as soon as the final inspection has taken place and all coating materials have been adequately cured according to the coating product(s) manufacturer’s recommendations.

END OF SECTION